SULTAN AZLAN SHAH POWER STATION
TNB JANAMANJUNG SDN BHD
CHEMICAL SERVICES AND ENVIRONMENT SECTION

MONTHLY REPORT
October 2019

- Environment Performance Update

| Parameter |  | Status / Description |
| --- | --- | --- |
| Stack monitoring | Unit M1 | All readings were within DOE limit except as mentioned below: - CO online analyser faulty for the whole month. - M1 under maintenance outage from 4 – 6 October 2019. - Opacity maximum reading exceeded DOE limit for 28 days suspect due to ESP rapping and maintenance activities but daily average reading below the DOE limit. |
|  | Unit M2 | All readings were within DOE limit except as mentioned below: - M2 under plant outage for whole month. |
|  | Unit M3 | All readings were within DOE limit except as mentioned below: - CO maximum reading exceeded limit for 1 day but daily average reading below limit. - Opacity maximum reading exceeded limit CAR 2014 for 10 days suspect due to ESP rapping and maintenance activities but daily average reading below the DOE limit |
|  | Unit M4 | All readings were within DOE limit except as mentioned below: - SO2 maximum readings exceeded limit for 8 days but daily average reading below the CAR 2014 DOE limit. - CO maximum reading exceeded limit for 7 days but daily average reading below the CAR 2014 DOE limit. - Dust maximum reading exceeded limit CAR 2014 for 28 days but daily average reading below limit. - Opacity maximum reading exceeded limit CAR 2014 for 28 days but daily average reading below limit. Opacity emission above 40% exceeded 5 min/hr for 2 days and exceed 15 min/day for days. |
| Rain Water | AQM No. 1 | Average pH reading was 4.92 |
|  | AQM No. 2 | Average pH reading was 5.37 |
|  | AQM No. 3 | Average pH reading was 5.27 |
| Ambient Air | AQM No. 1 | All readings were within DOE limit except as mention below: - PM2.5 exceeded maximum limit for 1 day suspected from road dust and haze. |
|  | AQM No. 2 | All readings were within DOE limit except as mention below: - PM10 exceeded maximum limit for 4 days suspected from road dust and haze. - PM2.5 exceeded maximum limit for 15 days suspected from road dust and haze. |
|  | AQM No. 3 | All readings were within DOE limit except as mention below: - PM10 exceeded maximum limit for 7 days suspected from road dust and haze. - PM2.5 exceeded maximum limit for 9 days suspected from road dust and haze. |
| Noise Level | NM1- North bank of island. | Day and night Leq dB readings within limit. |
|  | NM2- East bank of island | Day and night Leq dB readings within limit. |
|  | NM3- North bank of island (Middle) | Day and night Leq dB readings within limit. |
|  | NM4-West bank of island | Day and night Leq dB readings within limit. |
| GF 1 IWWTP Effluent |  | All parameters tested within DOE standard B limit |
| GF 2 IWWTP Effluent |  | All parameters tested within DOE standard B limit |
| GF1 CYWWTP Effluent |  | All parameters tested within DOE standard B limit. |
| GF2 CYWWTP Effluent |  | All parameters tested within DOE standard B limit |
| GF1 Cooling water | Fore bay | All parameters tested within the DOE standard B limit |
|  | Outfall | All parameters tested within the DOE standard B limit |
| GF2 Cooling water | Fore bay | All parameters tested within the DOE standard B limit |
|  | Outfall | All parameters tested within the DOE standard B limit |
| GF1 Storm water | N/A | All parameters tested within the DOE standard B limit. |
| GF2 Storm water | N/A | All parameters tested within the DOE standard B limit. |
| Scheduled Wastes Disposed (MT) | N/A | * No Disposal |

- Effluent (treated water) Discharged:

| NO. | PLANT | TOTAL DISCHARGED THIS MONTH m3 | TOTAL DISCHRAGED IN THIS FY m3 | REMARKS |
| --- | --- | --- | --- | --- |
| 1 | GF1 IWWTP | 36,982 | 333,770 |  |
| 2 | GF1 CYWWTP | 28,277 | 111,521 |  |
| 3 | GF2 IWWTP | 27,754 | 253,477 |  |
| 4 | GF2 CYWWTP | - | - | RECYCLED |
| TOTAL |  | 56,031 | 698,768 |  |

- List of activities related to environment in FY2019

| Date | Activities |
| --- | --- |
| 9-11 Jan 2019 | ISO:HSE Legal Requirements and Internal Audit Course/training (ISO9001,14001 & 45001) |
| 25 Feb-1 Mar 2019 | Internal Audit |
| 1 Apr 2019 | Environmental Management Review Meeting |
| 7 – 10 May 2019 | ISO14001:2015 SIRIM Surveillance Audit |
| 25 June 2019 | EMC meeting No. 1 FY2019 |
| 26 September 2019 | EMC meeting No. 2 FY2019 |

- Environmental achievement

| Description | ISEMS Score / Rating |  |  |
| --- | --- | --- | --- |
|  | FY 14/15 |  | FY 15/16 |
| ENVIRONMENTAL (EMS) AUDIT SCORE | 93.50% |  | 95.40% |